## SOW Tasks
Technician Scope of Works - CSS092
Tracker & sign‑off sheet
Project Details |  | General Notes / Preconditions
Project | CSS092 | • All works to comply with site WHS, isolation/LOTO and permit requirements. • Technician to confirm latest drawings/approved configuration before modifications. • Record pre‑works condition with photos; record any ‘as‑found’ defects as notes/NCRs. • Provide completion evidence: photos, test results (where applicable), and sign‑off.
Client | T2D
Site / Location | Adelaide, Waterloo
Work Order / Ref
Prepared By | Chris H
Prepared Date | 2026-03-16
Revision | 1
ID | Item | Task / Scope Description | Discipline | Priority | Dependencies / Permits | Acceptance Criteria / Tests | Assigned To | Status | % Complete | Planned Start | Planned Finish | Overdue | Actual Hours (from Log) | Completion Evidence
1 | Shunt Trip Design | Review CSS092 Sub 1 shunt trip matrix against drawings and confirm design intent for Q11-1 versus Q11-3 operation. | Protection | P1 - Critical | Issued drawings / schematic review. | Engineering confirmation issued that only E-stop should trip Q11-3; transformer-related trips act on Q11-1 only. | Mark Constable | Complete | 100 | 2026-02-24 | 2026-02-24 |  | 0 | 24/02/2026 Mark confirmed only the E-stop should trip Q11-3 and advised site metering test to confirm any unintended voltage on the Q11-3 shunt coil.
2 | Shunt Trip Verification | Perform on-site functional test of the shunt trip circuits, meter the Q11-3 shunt coil during temp/arc simulation, and rectify wiring if Q11-3 receives unintended trip voltage. | Protection | P1 - Critical | Shutdown / HV access permit; agreed test method; engineer support if rectification is required. | Q11-3 remains closed for transformer-related trip simulation and recorded test results show no unintended trip voltage applied to its shunt coil. | PBE Technician | In Progress | 50 |  |  |  | 0 | Engineering intent confirmed in email, but no searched email showed completed field verification or rectification sign-off.
3 | TX Temp Controller | Confirm BWD-3K130 transformer temperature controller operation using simulation mode and verify alarm / trip outputs for CSS092. | Testing | P2 - High | Shutdown / HV access and latest controller manual. | Simulation proves controller outputs operate correctly and test results are captured. | PBE Technician | In Progress | 50 |  |  |  | 0 | 27/02/2026 email set out intended operation and practical test steps, but no returned test record was sighted in the searched emails.
4 | Transformer Fan | Identify the faulty transformer fan motor / sensor, source a suitable spare or replacement, install it, and prove correct fan operation. | Mechanical | P2 - High | Shutdown of Sub 1 / batch plant; photos or nameplate details; parts availability. | Replacement fan / sensor fitted, fan fault cleared, and fan operation proven under controller output. | PBE Workshop | In Progress | 50 |  |  |  | 0 | 24/02/2026 to 05/03/2026 emails show the fan fault was raised, photos / nameplate details were requested, and PBE was looking to use a spare from another sub.
5 | Shutdown / Access | Coordinate weekend shutdown window, HV access permits, and technician availability for CSS092 fan / controller rectification works. | General | P2 - High | T2D production window, HV access permit, and technician availability. | Shutdown / permit confirmed and technician booked to complete outstanding rectification works. | Chris Hoogwerf | Blocked | 0 |  |  |  | 0 | 05/03/2026 Brendan advised site would be in full production from 16/03/2026 and outstanding works would need to move to weekends.
6 | Remote Start Cabling | Connect remote start controls into the CSS092 emergency genset and ATS during shutdown. | Switchboard | P1 - Critical | Approved shutdown / isolation window. | Remote start control cabling terminated and ready for functional testing. | James Schaedel / Adelpower | Complete | 100 | 2026-03-08 | 2026-03-08 |  | 0 | 10/03/2026 James advised that on Sunday 08/03/2026 the remote start controls were connected into the emergency genset and ATS.
7 | Remote Start Configuration | Diagnose and configure the CSS092 genset remote start digital input so the genset starts automatically from the ATS / remote input. | Testing | P1 - Critical | Laptop / configuration software for genset controller and commissioning window. | Genset starts in AUTO from remote / ATS input. | James Schaedel / Adelpower | Complete | 100 | 2026-03-10 | 2026-03-11 |  | 0 | 10/03/2026 James reported CSS092 would not start from remote input; 11/03/2026 he confirmed the CSS092 genset and ATS were commissioned and functional.
8 | ATS/Genset Commissioning | Complete CSS092 ATS and emergency genset functional commissioning. | Testing | P1 - Critical | Remote start input operational and site available for testing. | ATS and genset commissioned and functional. | James Schaedel / Adelpower | Complete | 100 | 2026-03-11 | 2026-03-11 |  | 0 | 11/03/2026 email from James: CSS092 genset and ATS is now commissioned and functional.
9 | Commissioning Closeout | Issue CSS092 commissioning closeout documents including SAT, eCoC, photos and test sheets. | Testing | P2 - High | SAT template and subcontractor closeout package. | SAT, eCoC, photos and test sheets issued to PBE / client. | James Schaedel / Adelpower | In Progress | 50 |  |  |  | 0 | 10/03/2026 James said eCoC / photos would follow after commissioning; 11/03/2026 he requested the SAT template; no final closeout package was sighted in the searched emails.
10 | Door Engineering Letter | Prepare and issue an engineering letter covering the as-installed door relocation workaround at CSS092 / associated substation works. | General | P2 - High | Engineer review of the as-installed workaround and supporting design information. | Engineering letter issued to T2D for the implemented workaround. | Engineering | Not Started | 0 | 2026-03-16 |  |  | 0 | 16/03/2026 Kyle advised the site had already moved the door and requested an engineering letter for the completed works.
11 | Generator Plant Induction | Arrange T2D plant induction for the two generators associated with CSS092 works. | General | P3 - Medium | T2D plant team requirements and generator details / documents. | Both generators inducted through the plant team. | Chris Hoogwerf | Not Started | 0 | 2026-03-16 |  |  | 0 | 16/03/2026 Kyle requested that the two generators be plant inducted through the T2D plant team.
Formulas:
Overdue = IF(AND([Planned Finish]<TODAY(),[Status]<>"Complete",[Planned Finish]<>""),"YES","")

## Lists (hidden)
Validation Lists
Status | Not Started | In Progress | Complete | On Hold | Blocked
Priority | P1 - Critical | P2 - High | P3 - Medium | P4 - Low
Area | Substation - MV | Substation - LV | HVDB0071 | Doors / Enclosure | Panels | Other
Discipline | Protection | Switchboard | Mechanical | Testing | General
YesNo | Yes | No
Technicians
TaskIDs | 1

## Daily Log
Technician Daily Log
Use this to capture daily hours; SOW pulls totals automatically.
Date | Technician | Task ID | Task Summary | Hours | Work Performed / Notes | Client/PM Initials

## Dashboard
SOW Dashboard
At-a-glance progress (driven from SOW Tasks)
Progress Summary
Total Tasks |  |  | Complete | In Progress
11 |  |  | 4 | 4
Blocked / On Hold |  |  | Overdue | Overall % Complete
1 |  |  | 0 | 54.5455
Status | Count
Not Started | 2
In Progress | 4
Complete | 4
On Hold | 0
Blocked | 1